## Sheet1
LCUB Watt Rd - Ava Data Substation Addition
1000 MCM Aluminum URD Cable Requirements
15kV Power Cable - 1,000 MCM Al. - Phase Conductor, cross-linked polyethylene
compacted Aluminum condutor, 15kV, 1,000 MCM Aluminum, 133% insulation
level, 220 Mil EPR insulated, with 1/3 concentric neutral, and PVC outer jacket.
| # per | # of | total | Length | Total
| phase | phases | runs | per run | footage
Ckt 1 | 1 | 3 | 3 | 250 | 750
Ckt 2 | 1 | 3 | 3 | 275 | 825
Ckt 3 | 1 | 3 | 3 | 325 | 975
Ckt 4 | 1 | 3 | 3 | 350 | 1050
| # per | # of | total | Length | Total
| phase | phases | runs | per run | footage
TX to SWGR | 6 | 3 | 18 | 215 | 3870
|  |  | Total Project Footage |  | 7470
* Based on specifications above, please include estimated reel size (and associated
weight) to minimize waste.