Water Distribution Plans Review Checklist

Project: 						Date of Review:

Engineer: 						Phone #:

Developer:						Phone #:

The list below is intended as a guide to the critical items required by the Tennessee Department of Environment and Conservation (TDEC) requirements and the Rules, Regulations, Rate and Policies of LCUB Water Department. The engineer is responsible for being familiar with and meeting the design standards of LCUB and TDEC. It is strongly suggested that a pre-design conference be schedule with a preliminary development layout including topography and sewer features available for the conference.

Requirements for General and Detailed Plans of Water Distribution Systems:

Approximate plan size 24” x 36”

Plans are clear and legible

Maximum Scale 50 feet per inch for plans and profiles – maximum vertical scale

of 10 feet per inch (Note: This is LCUB’s requirement and is stricter that TDEC)

Name of water system and county in which located

A Vicinity Map (location map) showing location of the project if a complete

system map is not included

___      Engineer name, address and phone number on first sheet of plans

Plans stamped and signed by Tennessee licensed engineer

A Key map showing location of detailed drawings when project is comprehensive

Developer and property owner’s name, address and phone number on first sheet

of plans

Servicing utility name, address and phone on the first sheet of plans. (Lenoir City

Utilities Board, 7698 Creekwood Park Boulevard, Lenoir City, TN 37772, (844)

687-5282)

Project layout map, project name, design date, graphic scale, north arrow, and

sheet numbers on all sheets

All text shall be legible and of sufficient size (measure 0.10 inches high when printed to scale)

Benchmarks (All plans to include the establishment of a minimum of one

benchmark for each project.  Benchmark and its elevation are to be shown on the

plan set.  Benchmark to be maintained through the completion of the project)

Lot lines and locations shown on all plan views including lot numbers

Street names and edge of pavement locations as well as right-of-way

Right-of-ways and Easements needed for the water line that falls inside/outside of

the property shall be signed and furnished prior to start of project

Inclusion of LCUB Current Water Construction Notes

Revisions tabulated on re-submittals

100-foot stationing of water lines and stationing of all appurtenances on plan and

any included profile views

Plan/Profile sheets shall be drawn for water lines 12 inches in diameter and larger

Existing utilities shall be field located whenever reasonable and the source of the

utility locations noted on the plans

Location of proposed service connections. Taps shall be spaced to avoid conflict

with other utilities, driveways, etc.

Location of proposed water lines in relations to roads, bridges and other

identifiable objects

Location of valves, fire hydrants, tees, reducers/enlargers, bends and other

appurtenances (Stationing)

Sufficient details shown on the plans to allow for material take off and location of

lines in the field by a third party

For all water lines, the relevant elevations of all pipelines and conflicting

structures at utility crossings shall be shown. This shall include a short profile

view of all utility crossings of the water line where new utility lines are being

constructed.

Location, size and material of all water lines and appurtenances relative to the

project – both existing and for construction

Stream crossings providing profiles with elevations of the stream bed and the

normal and extreme high and low water levels if this information is available

Reference all LCUB Standard Water Details on plans where applicable

All bodies of water including direction of flow and high-water elevations

Specialized Water Details:

Hydraulic profile or data and computations showing hydraulics or proposed

additions to the distribution system. (NOTE The City of Lenoir City Minimum

standards are 750 GPM fire flow with 30 PSI residual pressure-this exceeds

the State of Tennessee minimums. LCUB also requires the lowest and highest

static and residual pressure to be calculated and shown on the plans.)

For linear designs, plan and profile shall be on the same sheet and oriented in

generally the same direction.

Hydraulic profile or data and computations showing hydraulics or proposed

Include the radius of any turns where joint deflection is to be used to curve the

water line – For 8-inch pipe, the maximum deflection per joint is 5 degrees. For

curves tighter than this, please include appropriate bends as part of the plans.

Water Distribution System shall be minimum Six (6) inch C900 PVC, Class 200

(SDR21) PVC, HDPE (SDR11), or Ductile Iron Pipe (No Exceptions). Upon

review of plans, LCUB has the right to require the Water Distribution System to be Eight (8) inch pipe in-lieu of Six (6) inch.

Developer (Owner) and/or Contractor shall be responsible for installing three (3)

way valve clusters at all roadway intersections.

LCUB General Notes to be included on the drawings:

1. ALL WORK TO BE PERFORMED WILL BE IN ACCORDANCE WITH THE LENOIR CITY UTILITIES BOARD WATER DEPARTMENT (CURRENT EDITION) SPECIFICATIONS AND DETAILS.

2. PRE-CONSTRUCTION CONFERENCE SHALL BE CONDUCTED WITH THE LENOIR CITY UTILITIES BOARD REPRESENTATIVES, DESIGN ENGINEER, AND UTILITY CONTRACTOR PRIOR TO ANY UTILITIES CONSTRUCTION ACTIVITIES BEGINNING.

3. WATER LINE MATERIALS, INSTALLATION, TESTING AND DISINFECTION PER LENOIR CITY UTILTIES BOARD WATER DEPARTMENT STANDARDS (CURRENT EDITION).

4. CONTRACTOR SHALL INSTALL ALL WATER SERVICES.  SERVICE LINES FOR SINGLE WATER METERS SHALL BE ¾-INCH DIAMETER AND SERVICE LINES FOR DOUBLE WATER METERS SHALL BE 1-INCH DIAMETER.  MATERIALS AND FITTINGS SHALL BE INSTALLED IN ACCORDANCE WITH THE SPECIFICATIONS AND TYPICAL DETAIL W7.

5. ALL CONSTRUCTION AND TESTING ACTIVITIES MUST BE OBSERVED BY A RESIDENT PROJECT REPRESENTATIVE (RPR) AS DESIGNATED BY LCUB.  WORK PERFORMED WITHOUT DESIGNATED RPR OVERSIGHT AND APPROVAL SHALL NOT BE ACCEPTED BY LCUB.

6. ALL COSTS INCURRED BY LCUB FOR PROJECT-RELATED RPR AND GENERAL ENGINEERING SERVICES DURING CONSTRUCTION SHALL BE REIMBURSED BY THE PROPERTY OWNER/DEVELOPER.

7. ALL PROJECT CLOSEOUT DOCUMENTS MUST BE PROVIDED BY THE OWNER/DEVELOPER PRIOR TO LCUB ACCEPTING OWNERSHIP OF NEW FACILITIES AS FOLLOWS:

A.  RECORD DRAWINGS WITH APPROVED MODIFICATIONS TO DESIGN DRAWINGS IN RED

B.  RPR DAILY REPORTS

C.  CONSTRUCTION PHOTOS

D.  RPR TESTING REPORTS

E.  PRE-CONSTRUCTION AND CONSTRUCTION PHOTOGRAPHS

F. VERIFIED GIS DATA COLLECTED BY LCUB-APPROVED  STAFF

G.  ASSOCIATED EASEMENT DOCUMENTS

H. FLUSHING / WATER LOSS REPORTS / BACTERIOLOGICAL    RESULTS

8. CONTRACTOR SHALL PROVIDE EROSION AND SEDIMENT CONTROL FOR ALL EXCAVATIONS.

9. CONTRACTOR SHALL PERFORM ALL WATER LINE TAPS REQUIRED.

10. FIRE HYDRANTS SHALL BE MUELLER SUPER CENTURION #250 (FACTORY POWDER COATED YELLOW – OPEN COUNTERCLOCKWISE), WITH 5 ¼” OPENING VALVE. HYDRANTS SHALL BE PAINTED AS SHOWN BELOW, IN ACCORDANCE WITH THE LATEST NFPA CODE FOR MARKING HYDRANTS, AND/OR IN ACCORDANCE WITH THE LENOIR CITY FIRE DEPARTMENT STANDARDS.

RED			LESS THAN 500 GAL./MIN.

ORANGE		500 – 999 GAL./MIN.

GREEN			1000 – 1499 GAL./MIN.

LIGHT BLUE		1500 GAL./MIN. OR GREATER

11. MAXIMUM ALLOWABLE DEFLECTION OF AWWA C111 DUCTILE IRON PIPE PUSH ON JOINTS IS FIVE DEGREES PER JOINT.  A DEFLECTION GREATER THAN THIS WILL REQUIRE ADEQUATE FITTINGS TO DEFLECT THE PIPE.

12. BLASTING NOT PERMITTED.

13.  CONTRACTOR IS REPONSIBLE FOR EMPLOYING ALL TRAFFIC CONTROL MEASURES AS NECESSARY IN ACCORDANCE WITH PROJECT SPECIFICATIONS SECTION 01570-TRAFFIC REGULATIONS, AND MUTCD.

14. DEVELOPER (OWNER) AND/OR CONTRACTOR SHALL BE RESPONSIBLE FOR ANY EXISTING WATER DISTRIBUTION IMPROVEMENTS REQUIRED TO PROVIDE ADEQUATE WATER PRESSURE AND FIRE FLOW TO THE NEW DEVELOPMENT AND MAINTAIN EXISTING DISTRIBUTION SYSTEM PRESSURES.

15. DEVELOPER (OWNER) AND/OR CONTRACTOR SHALL BE RESPONSIBLE FOR INSTALLING ALL WATER TAPS, SERVICE LINES, METER YOLKS, AND CASINGS PER LCUB STANDARD SPECIFICATIONS FOR THE NEW DEVELOPMENT.

16. DEVELOPER (OWNER) AND/OR CONTRACTOR SHALL BE RESPONSIBLE FOR INSTALLING ALL FIRE HYDRANTS AND APPURTENANCES PER LCUB STANDARD SPECIFICATIONS FOR THE NEW DEVELOPMENT.  SPACING BETWEEN FIRE HYDRANTS SHALL NOT EXCEED 600 FEET AND HOSE PULL LENGTH (AS MEASURED FROM THE BACK OF THE FURTHEST PROPOSED STRUCTURE TO THE CLOSEST FIRE HYDRANT ALONG THE ROADWAY) SHALL NOT EXCEED 500 FEET.  TYPICAL REQUESTED FIRE HYDRANT LOCATIONS ARE AT ROAD INTERSECTIONS.

17. ASSOCIATED WATER FEES FOR DEVELOPMENT PROJECTS SHALL INCLUDE, BUT NOT LIMITED TO, TAPS, CAPITAL RESERVE, SPECIAL ASSESSMENT, ETC. AND SHALL BE BILLED AT THE END OF EACH PROJECT PHASE AND PAYMENT SHALL BE DUE FROM DEVELOPER AT THAT TIME.  WATER SERVICE SHALL NOT BE MADE LIVE UNTIL PAYMENT IS RECEIVED IN FULL.

18. LCUB HAS THE RIGHT TO REQUIRE A LARGER DIAMETER PIPE SIZE OR DUCTILE IRON PIPE BASED UPON HYDRAULIC ANALYSIS, DEPTH, SOIL, AND FUTURE CONDITIONS.

19. WATER DISTRIBUTION SYSTEM SHALL BE MINIMUM SIX (6) INCH C900 PVC, CLASS 200 (SDR21) PVC, HDPE (SDR 11), OR DUCTILE IRON PIPE (NO EXCEPTIONS). UPON REVIEW OF PLANS, LCUB HAS THE RIGHT TO REQUIRE THE WATER DISTRIBUTION SYSTEM TO BE EIGHT (8) INCH PIPE IN LIEU OF SIX (6) INCH.

___      20. RIGHT-OF-WAYS AND EASEMENTS NEEDED FOR THE WATER LINE THAT FALLS INSIDE/OUTSIDE OF THE PROPERTY SHALL BE SIGNED AND FURNISHED PRIOR TO START OF PROJECT

___     21. CONTRACTOR SHALL FIELD VERIFY AND POTHOLE ALL UTILITIES AS INDICATED BY DRAWING, GIS, TENNESSEE ONE-CALL, ETC.

___   22. ALL CONTRACTORS SHALL BE LICENSED CONTRACTORS WITH “MU” CLASSIFICATION IN THE STATE OF TENNESSEE AS REQUIRED BY THE CONTRACTOR’S LICENSING ACT OF 1994 AND RELATED AMENDMENTS THERETO.

NOTE: 	WATER NOTES ARE SUBJECT TO CHANGE